## Sheet1
SL.NO. | PARTICULARS | UNITS | QUANTITY | UNIT RATE SUPPLY (Rs.) |  |  | Total Supply Amount (Including Taxes) | UNIT RATE E & C (Rs.) |  |  | Total E&C Amount (Including Taxes) | Total
|  |  |  | Supply Rate | supply amount | Taxes (GST Etc.) (Indicate % here) |  | E & C Rate (Basic) | GST Tax (Indicate % here) | Errection Amount
v | Fire Alarm Panel
1A | Main Fire Alarm Panel (4 LOOP) Supply, Installation, Testing & Commissioning of Addressable Fire Alarm Control Panel having min 250 devices Loop capacity.Minimum 600 character blue LCD with backlight illumination display and TCP/IP communication. Panel Shall integrate with Control, Monitor, Relay modules, Duct Detectors, Beam Detectors. Panel should have 30Min battery backup in Alarm condition & 24hrs in normal condition. | Nos. | 0 | 178200 | 0 | 18% | 0 | 15000 | 18% | 0 | 0 | 0
1B | Main Fire Alarm Panel (2 LOOP) Supply, Installation, Testing & Commissioning of Addressable Fire Alarm Control Panel having min 250 devices Loop capacity.Minimum 600 character blue LCD with backlight illumination display and TCP/IP communication. Panel Shall integrate with Control, Monitor, Relay modules, Duct Detectors, Beam Detectors. Panel should have 30Min battery backup in Alarm condition & 24hrs in normal condition. | Nos. | 0 | 157000 | 0 | 18% | 0 | 12000 | 18% | 0 | 0 | 0
1C | Main Fire Alarm Panel (1 LOOP) Supply, Installation, Testing & Commissioning of Addressable Fire Alarm Control Panel having min 250 devices Loop capacity.Minimum 600 character blue LCD with backlight illumination display and TCP/IP communication. Panel Shall integrate with Control, Monitor, Relay modules, Duct Detectors, Beam Detectors. Panel should have 30Min battery backup in Alarm condition & 24hrs in normal condition. | Nos. | 0 | 81500 | 0 | 18% | 0 | 10000 | 18% | 0 | 0 | 0
1D | LCD Repeater Panel Supply, Installation, Testing & Commissioning of repeater panel, 640 characters; The LCD shall display all events/detectors, device status of complete systems in the network. | Nos. | 1 | 46000 | 46000 | 18% | 54280 | 6000 | 18% | 6000 | 7080 | 61360
2 | Detectors
2A | Addressable Multi Sensor Detector Supply, Installation, Testing & Commissioning of Addressable Multisensor detector with LED, Detector base & necessary accessories to mount the detector like JB,cable glands etc. | Nos | 21 | 2700 | 56700 | 18% | 66906 | 375 | 18% | 7875 | 9292.5 | 76198.5
2B | Beam Detector with reflector Supply, Installation, Testing & commissioning of Beam detector with all required mounting accessories. Having the coverage distance ranging from 5m to 100m. The transmitter and receiver shall be combined in a single housing. 10 to 32VDC power source. Detector shall communicate 3 danger levels for differentiated alarm activation on the controller as well individual relay output to interface with FAS Panel. Detector should quote along with necessary mounting accessories like JB, Cable Glands. | Nos | 0 | 35500 | 0 | 18% | 0 | 5500 | 18% | 0 | 0 | 0
2C | Beam Detector Controller | Nos | 0 | 12850 | 0 | 18% | 0 | 2500 | 18% | 0 | 0 | 0
2D | Optical Smoke Imaging Detector (OSID) Supply, Installation, Testing & commissioning of OSID detector worked on UV & IR rays with all required mounting accessories. Having the coverage distance ranging from 5m to 100m. The transmitter and receiver shall be combined in a single housing. 10 to 32VDC power source. Detector shall communicate 3 danger levels for differentiated alarm activation on the controller as well individual relay output to interface with FAS Panel. Detector should quote along with necessary mounting accessories like JB, Cable Glands. | QRO | 0 | 79060 | 0 | 18% | 0 | 12500 | 18% | 0 | 0 | 0
2E | Heat Detector (Rate of Rise) Supply, Installation, Testing & Commissioning of Addressable Heat detector with LED, Detector base & necessary accessories to mount the detector like JB,cable glands etc. | QRO | 0 | 2700 | 0 | 18% | 0 | 375 | 18% | 0 | 0 | 0
3 | Alarm Initiating Devices
3A | Indoor Manual Call Point Supply, Installation,Testing & Commissioning of Addressable Manual call point (MCP Dual Action type). Semi-Flush or Surface mounting with necessary accessories and Cable Glands. | Nos | 4 | 4080 | 16320 | 18% | 19257.6 | 375 | 18% | 1500 | 1770 | 21027.6
4 | Audio & Visual Notification Device
4A | Indoor Hooter cum Strobe Supply, Installation, Testing & Commissioning of of FM Approved Strobe cum Sounder. Sounder output up to 98DB and Lights with 110 cd. Unit should quote along with Power Supply & necessary mounting accessories like JB, Cable Glands. | Nos | 4 | 4150 | 16600 | 18% | 19588 | 375 | 18% | 1500 | 1770 | 21358
5 | Modules
5A | Control Module (For Hooters) Supply,Installation,Testing & Commissioning of Listed Addressable Control Module with necessary accessories. | Nos | 4 | 3950 | 15800 | 18% | 18644 | 375 | 18% | 1500 | 1770 | 20414
5B | Control Relay Module for 3rd Party Integration Supply,Installation,Testing & Commissioning of Listed Addressable Control Module with necessary accessories. | Nos. | 1 | 3950 | 3950 | 18% | 4661 | 375 | 18% | 375 | 442.5 | 5103.5
5C | Monitor Module (For Conventional Detectors) Supply,Installation,Testing & Commissioning of Addressable Monitor Module with necessary accessories. | Nos | 0 | 3950 | 0 | 18% | 0 | 375 | 18% | 0 | 0 | 0
5D | Monitor Module (For Fire doors feedback signal) Supply,Installation,Testing & Commissioning of Addressable Monitor Module with necessary accessories. | Nos | 0 | 3950 | 0 | 18% | 0 | 375 | 18% | 0 | 0 | 0
5E | Relay Module for Future interface with any AHU, Damper if any | Nos | 1 | 6450 | 6450 | 18% | 7611 | 375 | 18% | 375 | 442.5 | 8053.5
5F | Input Module for pumproom feedback signal | Nos | 8 | 4850 | 38800 | 18% | 45784 | 375 | 18% | 3000 | 3540 | 49324
5G | Limit switch for fire doors | Nos | 0 | 1050 | 0 | 18% | 0 | 375 | 18% | 0 | 0 | 0
5H | Fault Isolator Module Supply,Installation,Testing & Commissioning of Addressable Fault Isolator Module with necessary accessories. | Nos | 0 |  | 0 | 18% | 0 |  | 18% | 0 | 0 | 0
5I | Response Indicator Supply,Installation,Testing & Commissioning of Response Indicators | Nos. | 0 | 110 | 0 | 18% | 0 | 100 | 18% | 0 | 0 | 0
5J | Power Supply Unit Supply & Installation, Testing & Commissioning of 24 Vdc Power supply for the Beam Detector with suitable enclosure & required accessories for mounting. | Nos | 0 | 7500 | 0 | 18% | 0 | 1000 | 18% | 0 | 0 | 0
6 | Cables and accessories
6A | 2Cx1.5 mm2, Armoured Cable Supply & laying of 2C x 1.5 mm2, Stranded Copper conductor, PVC screened FRLS insulated, Shielded, Armoured Cable, GI saddle spacers every 0.3 mtr , complete termination & Ferruling (Color should be RED) | Mtr | 300 | 95 | 28500 | 18% | 33630 | 72 | 18% | 21600 | 25488 | 59118
6B | Fiber optic convertor | Nos. | 0 | 16500 | 0 | 18% | 0 | 1200 | 18% | 0 | 0 | 0
6C | Fiber optics Cable with accessories | Mtr | 0 | 65 | 0 | 18% | 0 | 180 | 18% | 0 | 0 | 0
6D | 25 MM METAL CONDUIT Supply & laying of 25mm metal conduit with all required mounting accessories. | Mtr | 50 | 294 | 14700 | 18% | 17346 | 250 | 18% | 12500 | 14750 | 32096
6E | 50MM x 40MM Perforated Cable Tray: Supply & laying of 2mm thick perforated cable tray with cover and with all required mounting accessories | Mtr | 0 | 455 | 0 | 18% | 0 | 120 | 18% | 0 | 0 | 0
| Total Amount |  |  |  | 243820 |  | 287707.6 |  |  | 56225 | 66345.5 | 354053.1
vi | PORTABLE FIRE EXTINGUISHERS
1 | CO2 type Fire Extinguisher 4.5 Kg Capacity made from brand new PESO/CCOE approved seamless steel cylinder as per IS:7285 fitted with discharge hose and horn with wheel type valve and initial charge as per 15683:2018 bearing ISI Mark. | NO | 4 | 7365 | 29460 | 18% | 34762.8 | 275 | 18% | 1100 | 1298 | 36060.8
2 | ABC Dry Powder (MAP 50%) Stored Pressure type Fire Extinguisher 4 Kg Capacity with Hose & Nozzle, BIS Approved for fighting ABC Class of Fire. The Extinguisher will be manufactured strictly as per IS:15683:2018 bearing ISI Mark. | NO | 8 | 3319 | 26552 | 18% | 31331.36 | 275 | 18% | 2200 | 2596 | 33927.36
3 | Mechanical Foam Stored Pressure, Portable Type Fire Extinguisher 9 Litres Capacity fitted with controllable discharge mechanism with EPDM hose & air aspirated nozzle, CE marked valve with in-built NRV & safety release provision and AFFF (3%) Agent. External pure polyester powder coated (UV resistant) and internal plastic lining. The extinguisher is manufactured as per IS:15683:2018 bearing ISI & CE Mark. | NO | 4 | 3085 | 12340 | 18% | 14561.2 | 275 | 18% | 1100 | 1298 | 15859.2
4 | Mechanical Foam type Fire Extinguisher 45 Litres Capacity fitted with brass forged cap, MS neck ring, syphon tube, CO2 Gas Cartridge 300 gms as per IS:4947 and AFFF (6%) Agent. Extinguisher is phosphated and epoxy powder coated internally and externally and externally epoxy powder coated as per IS:5 Shade No. 538. The Extinguisher is manufactured as per IS:16018:2012 bearing ISI Mark. | NO | 1 | 11520 | 11520 | 18% | 13593.6 | 550 | 18% | 550 | 649 | 14242.6
| TOTAL |  |  |  | 79872 |  | 94248.96 |  |  | 4950 | 5841 | 100089.96
vii | ELECTRICAL
22 | DESIGN, MANUFACTURE, PACKING, FORWARDING, TRANSPORTATION AND DELIVERY AT SITE, UNLOADING, STORAGE AT SITE, SHIFTING FROM THE PLACE OF STORAGE TO INSTALLATION PLACE, UNPACKING, INSTALLATION WITH ALL FITTINGS AND ACCESSORIES, TESTING & COMMISSIONING, GETTING APPROVALS FROM ALL STATUTORY AUTHORITIES TO CARRY OUT ELECTRICAL WORK OF FIRE FIGHTING SYSTEM. BREAK UP GIVEN BELOW IS FOR REFERENCE/BILLING PURPOSE ONLY.
BREAK UP OF 'A' ABOVE
1 | LT SWITCHGEAR PANELS
1.1 | FIRE PANEL (MCC PANEL): 415V, 50Hz, short circuit rating 16kA/1Sec, indoor type, floor mounted, single front type, metal enclosed design, compartmentalised construction with copper busbars, form - 4A, IP-52, top cable entry with fixed type, TPN MCCB as incomer and TP/TPN MCCB/MPCB outgoing modules with DOL & Star Delta Starters, associated annunciations/indications/push buttons & other components/accessories. TYPE-2 coordination shall be ensured for all motor feeders. | NO | 1 | 552594 | 552594 | 18% | 652060.92 | 20350 | 18% | 20350 | 24013 | 676073.92
1.2 | Automatic Diesel Engine Control Panel for Standby Pump with built-in Battery Charger | NO | 1 | 60000 | 60000 | 18% | 70800 | 5500 | 18% | 5500 | 6490 | 77290
2 | LT POWER / CONTROL CABLES
1100 Voltage grade, Multistranded Aluminium/Copper Conductor, XLPE insulated, inner & outer extruded, inner and outer PVC sheathed, galvanised steel flat strip/round wire armoured power/control cables of following sizes to be laid overhead inside cable trays from Fire Hydrant Panel to equipments. Miscellaneous items such as clamp, cleat cable tags etc. as well as cable trays with necessary supports are included in the scope. Removal of empty drums as instructed by client is included in the scope.
2.1 | Power Cables from Fire Panel to Main Fire Water Pump (With Star Delta Starters)
2.2 | Power Cables from Fire Panel to Jockey Pump (With DOL Starters)
2.3 | Cable Sizes
a) | 3.5 C X 240 sq. mm A2XFY | M | 70 | 1012.704 | 70889.28 | 18% | 83649.3504 | 198 | 18% | 13860 | 16354.8 | 100004.1504
b) | 3 C X 16 sq. mm A2XFY | M | 25 | 138.096 | 3452.4 | 18% | 4073.832 | 72 | 18% | 1800 | 2124 | 6197.832
2.4 | 1100 Voltage grade, Multistranded Copper Conductor, XLPE insulated, inner & outer extruded, inner PVC sheathed & outer FRLS PVC sheathed, galvanised steel round wire armoured control cables of following sizes:
a) | 14 C X 1.5 sq. mm 2XWY | M | 25 | 437.304 | 10932.6 | 18% | 12900.468 | 88 | 18% | 2200 | 2596 | 15496.468
b) | 2 C X 1.5 sq. mm 2XWY | M | 250 | 121 | 30250 | 18% | 35695 | 83 | 18% | 20750 | 24485 | 60180
3 | LT CABLE TERMINATION
Cable terminations for XLPE insulated, PVC sheathed, 1.1 kV, Armoured Aluminium/Copper Conductor, power/control cables including stripping of cable insulation, supply and fixing of aluminium lugs for aluminium cables and tinned plated copper lugs for copper cables and crimping the same to the conductor, supply and fixing of double compression cable glands for below cable sizes as required.
1100 Voltage grade, Multistranded Aluminium/Copper Conductor, XLPE insulated, inner and outer PVC sheathed, galvanised steel flat strip/round wire armoured power cables.
3.1 | Cable Terminations
a) | 3.5 C X 240 sq. mm A2XFY | NO | 8 | 1519.056 | 12152.448 | 18% | 14339.8886 | 198 | 18% | 1584 | 1869.12 | 16209.0086
b) | 3 C X 16 sq. mm A2XFY | NO | 2 | 383.6 | 767.2 | 18% | 905.296 | 83 | 18% | 166 | 195.88 | 1101.176
3.2 | 1100 Voltage grade, Multistranded Copper Conductor, XLPE insulated, inner & outer extruded, inner PVC sheathed & outer FRLS PVC sheathed, galvanised steel round wire armoured control cables of following sizes:
a) | 14 C X 1.5 sq. mm 2XWY | NO | 2 | 288.4672 | 576.9344 | 18% | 680.7826 | 88 | 18% | 176 | 207.68 | 888.4626
b) | 2 C X 1.5 sq. mm 2XWY | NO | 50 | 121 | 6050 | 18% | 7139 | 83 | 18% | 4150 | 4897 | 12036
4 | CABLE TRAYS
4.1 | Readymade 2500 mm standard length, prefabricated, ladder/perforated cable tray pregalvanised of following sizes and associated accessories such as coupler plates, tees, elbows etc. 50 mm side flanges for perforated trays & 75 mm side flanges for ladder type cable trays shall be provided on both sides of the tray.
a) | 300 mm width (Vertical ladder type cable tray with cover) | M | 10 | 2761.92 | 27619.2 | 18% | 32590.656 | 275 | 18% | 2750 | 3245 | 35835.656
b) | 300 mm width (Horizontal ladder type cable tray) | M | 15 | 2071.44 | 31071.6 | 18% | 36664.488 | 275 | 18% | 4125 | 4867.5 | 41531.988
c) | 150 mm width (Vertical perforated type cable tray with cover) | M | 10 | 1407.0448 | 14070.448 | 18% | 16603.1286 | 193 | 18% | 1930 | 2277.4 | 18880.5286
d) | 75 mm width (Vertical perforated type cable tray with cover) | M | 20 | 1000.4288 | 20008.576 | 18% | 23610.1197 | 154 | 18% | 3080 | 3634.4 | 27244.5197
e) | 150 mm width (Horizontal perforated type cable tray) | M | 10 | 1407.0448 | 14070.448 | 18% | 16603.1286 | 193 | 18% | 1930 | 2277.4 | 18880.5286
f) | 75 mm width (Horizontal perforated type cable tray) | M | 8 | 1000.4288 | 8003.4304 | 18% | 9444.0479 | 154 | 18% | 1232 | 1453.76 | 10897.8079
4.2 | Cable tray supports, supporting frame for mounting of Swgr. Pnl./Control Panels etc. The supports shall be painted with 2 coats of red oxide primer and 2 coats of aluminium paint. Type of structural items required shall be ISMC 100, ISMC 75, ISA 50x50x6mm, ISA 65x65x6, ISA 40x40x3, MS plate 6mm, MS plate 10 mm or any other size as per requirement. | TON | 0.3 | 95900 | 28770 | 18% | 33948.6 | 44000 | 18% | 13200 | 15576 | 49524.6
NOTE: The rates shall be inclusive of bends/tees/cable markers etc.
5 | EARTHING SYSTEM
5.1 | Earthing system including supply, installation, testing and commissioning of G.I earthing strips/wires of following sizes to be laid in cable trays/on wall including jointing by welding, connecting to equipment, painting to welded portions by black bitumen paint. Necessary hardware is included in the scope. This includes earthing for fire hydrant system equipments as per latest version of IS:3043. For outdoor areas excavation, backfilling and removal of excess soil etc. is included in scope.
a) | 50 X 6 mm G.I. STRIP | M | 40 | 444.976 | 17799.04 | 18% | 21002.8672 | 94 | 18% | 3760 | 4436.8 | 25439.6672
b) | 25 X 6 mm G.I. STRIP | M | 30 | 230.16 | 6904.8 | 18% | 8147.664 | 72 | 18% | 2160 | 2548.8 | 10696.464
c) | 8 SWG GI WIRE | M | 20 | 230.16 | 4603.2 | 18% | 5431.776 | 72 | 18% | 1440 | 1699.2 | 7130.976
5.2 | Treated earth pits as per CEIG specific requirements. 40 mm Internal Diameter, Heavy Duty 3000 mm long GI pipe (Class B or better). Earth pit as per latest version of IS:3043. The earth pit shall be provided with 50 x 6 mm GI Strip up to chamber, disconnecting links with 600 x 600 mm (clear) brick chamber & 3mm thick CI chequered plate cover with hinge. Bentonite shall be provided for earth pits. Excavation, backfilling, removal of excess soil is included in the scope. | NO | 1 | 25778 | 25778 | 18% | 30418.04 | 8800 | 18% | 8800 | 10384 | 40802.04
| TOTAL |  |  |  | 946363.6048 |  | 1116709.0537 |  |  | 114943 | 135632.74 | 1252341.7937
viii | INSTRUMENTATION
1 | Level Switch for Fire Water Storage Tank | NO | 2 | 14576.8 | 29153.6 | 18% | 34401.248 | 1650 | 18% | 3300 | 3894 | 38295.248
2 | Pressure Gauge, Bourdon Type, 100 mm Dial and ½" NPT Bottom Connection | NO | 5 | 675.136 | 3375.68 | 18% | 3983.3024 | 385 | 18% | 1925 | 2271.5 | 6254.8024
3 | Pressure Switch, SPDT, Measuring Element - Bellows | NO | 9 | 5447.12 | 49024.08 | 18% | 57848.4144 | 385 | 18% | 3465 | 4088.7 | 61937.1144
4 | 200 NB Flow Meter | NO | 1 | 268520 | 268520 | 18% | 316853.6 | 1650 | 18% | 1650 | 1947 | 318800.6
| TOTAL |  |  |  | 350073.36 |  | 413086.5648 |  |  | 10340 | 12201.2 | 425287.7648